## Seismic Design Supplement
Practice Tip – PT.35
Version 1.2
Attachment 1a
Seismic Hazard Index Calculation - Examples
These are representatve samples only, provided for comparison purposes.
Elementary School in Toronto |  |  |  |  | OBC REFERENCE
Importance Category | Low | Normal | High | Post-disaster | 4.1.2.1.(3). & 5.2.2.1.(2)
Site Class (A, B, C, D, E, F; Refer to Geotechnical Report) |  |  |  | Stiff Soil: D | 4.1.8.4.
Earthquake Importance factor (IE ULS) |  |  |  | 1.3 | T.4.1.8.5.
Acceleration Based Coefficient (Fa) |  |  |  | 1.3 | T.4.1.8.4.B
5% Spectral Response Acceleration Sa(0.2) |  |  |  | 0.22 | 4.1.8.4.(1) & SB-1, T.1.2.
Seismic Hazard Index IEFaSa(0.2) = |  |  |  | 0.37 | 4.1.8.18.(1)
Design for Seismic Required for Categories 6 to 21, Table 4.1.1.18. (Equal or Above 0.35?) |  |  |  | YES | 4.1.8.18.(2)
An elementary school is a High Importance Category. This example in Toronto has typical soil (Stiff: D). The Seismic Hazard Index calculation result is above 0.35 and thus seismic design for non-structural elements is Required.
Office Building in Toronto |  |  |  |  | OBC REFERENCE
Importance Category | Low | Normal | High | Post-disaster | 4.1.2.1.(3). & 5.2.2.1.(2)
Site Class (A, B, C, D, E, F; Refer to Geotechnical Report) |  |  |  | Stiff Soil: D | 4.1.8.4.
Earthquake Importance factor (IE ULS) |  |  |  | 1 | T.4.1.8.5.
Acceleration Based Coefficient (Fa) |  |  |  | 1.3 | T.4.1.8.4.B
5% Spectral Response Acceleration Sa(0.2) |  |  |  | 0.22 | 4.1.8.4.(1) & SB-1, T.1.2.
Seismic Hazard Index IEFaSa(0.2) = |  |  |  | 0.29 | 4.1.8.18.(1)
Design for Seismic Required for Categories 6 to 21, Table 4.1.1.18. (Equal or Above 0.35?) |  |  |  | NO | 4.1.8.18.(2)
An office building is Normal Importance Category. An area in Toronto with typical soil (Stiff: D). The calculations result in a Seismic Hazard Index below 0.35 and thus seismic design for non-structural elements is Not Required.
Office Building in Ottawa |  |  |  |  | OBC REFERENCE
Importance Category | Low | Normal | High | Post-disaster | 4.1.2.1.(3). & 5.2.2.1.(2)
Site Class (A, B, C, D, E, F; Refer to Geotechnical Report) |  |  |  | Stiff Soil: D | 4.1.8.4.
Earthquake Importance factor (IE ULS) |  |  |  | 1 | T.4.1.8.5.
Acceleration Based Coefficient (Fa) |  |  |  | 1.1 | T.4.1.8.4.B
5% Spectral Response Acceleration Sa(0.2) |  |  |  | 0.64 | 4.1.8.4.(1) & SB-1, T.1.2.
Seismic Hazard Index IEFaSa(0.2) = |  |  |  | 0.7 | 4.1.8.18.(1)
Design for Seismic Required for Categories 6 to 21, Table 4.1.1.18. (Equal or Above 0.35?) |  |  |  | YES | 4.1.8.18.(2)
An office building in Ottawa with the same soil (Stiff: D). The Sa(0.2) is almost 3 times that of Toronto and the calculation for Seismic Hazard Index is above 0.35 - seismic design for non-structural elements is Required.
Warehouse in Ottawa |  |  |  |  | OBC REFERENCE
Importance Category | Low | Normal | High | Post-disaster | 4.1.2.1.(3). & 5.2.2.1.(2)
Site Class (A, B, C, D, E, F; Refer to Geotechnical Report) |  |  |  | Stiff Soil: D | 4.1.8.4.
Earthquake Importance factor (IE ULS) |  |  |  | 0.8 | T.4.1.8.5.
Acceleration Based Coefficient (Fa) |  |  |  | 1.1 | T.4.1.8.4.B
5% Spectral Response Acceleration Sa(0.2) |  |  |  | 0.64 | 4.1.8.4.(1) & SB-1, T.1.2.
Seismic Hazard Index IEFaSa(0.2) = |  |  |  | 0.56 | 4.1.8.18.(1)
Design for Seismic Required for Categories 6 to 21, Table 4.1.1.18. (Equal or Above 0.35?) |  |  |  | YES | 4.1.8.18.(2)
Due to the low Sa(0.2) value in the Ottawa area, even a Low Importance Category warehouse has a Seismic Hazard Index value above 0.35 - seismic design for non-structural elements is Required.